SECTION 01 68 00

EQUIPMENT AND VALVE IDENTIFICATION

PART 1 – GENERAL

  - SCOPE

- This section covers the furnishing and installation of nameplates and tags for identification of equipment, valves, panels, and instruments.

  - GENERAL

- Except as otherwise specified in equipment, valve, and instrumentation sections, nameplates and tags shall be as specified herein. Nameplates or tags shall be provided for all equipment, valves, operator interfaces, control and electrical panels, cabinets, instruments, and instrument racks that have been named and/or tagged on the Drawings.

1.03 SUBMITTALS

- Drawings and data shall be submitted in accordance with the requirements of the Submittals Procedures section for each type of tag provided including materials, colors, sizes, letter sizes, and installation instructions.

  - RELATED SECTIONS

(This section can be removed if there are no specific documents the designer feels should be called out.)

- 26 05 53 ELECTRICAL IDENTIFICATION

- 33 32 19 PUMP STATION

- 40 91 00 PRESSURE TRANSDUCERS

PART 2 - PRODUCTS

2.01 EQUIPMENT NUMBER PLATES

- All equipment tagged on the drawings, except for submerged equipment shall be provided with number plates bearing the equipment tag number identified on the Drawings.  Number plates shall be beveled; 1/8th inch thick laminated black phenolic plastic engraving stock with white core.  Lettering on number plates shall be capitalized block letters ¾ inch high. Number plate height shall be twice the letter height.  Number plate length shall be as needed, with suitable margins all around.  Lettering shall be placed in one row where practicable; however, where necessary due to excessive length, lettering shall be placed on more than one row and centered.

- Number plates shall be attached with stainless steel pan head screws, rivets, or drive screws.

- When a number plate cannot be installed due to the physical size, space, or mounting surface geometry of the equipment, the CONTRACTOR shall provide a 12-gauge stainless steel tag with engraved or imprinted equipment tag number.  Lettering on tags shall be ¼ inch high.  Tags shall be rectangular with smooth edges, and shall be fastened to the equipment with stainless steel mechanical fasteners or with a stainless steel chain.

2.02 EQUIPMENT INFORMATION PLATES

- Equipment shall be provided with engraved or stamped equipment information plates securely affixed with mechanical fasteners to the equipment in an accessible and visible location.  Equipment information Plates shall be in addition to the number plates specified.  Equipment information plates shall indicate the manufacturer’s name, address, product name, catalog number, serial number, capacity, operating and power characteristics, labels of tested compliances, and any other pertinent design data.  Equipment information plates listing the distributing agent only will not be acceptable.

2.03 VALVE AND GATE TAGS

- Temporary Tags - Each valve and gate with an identifying number indicated on the drawings or listed in the valve or gate schedule, shall be tagged or marked in the factory with the identifying number.

- Permanent Tags  - All valves and gates, except buried or submerged valves, that have been assigned a number on the Drawings or in the valve or gate schedule, shall be provided with a permanent number plate.  Tags shall be permanently attached to valves and gates with stainless steel mechanical fasteners or with stainless steel chains.  Numerals shall be ¾ inch high and shall be black baked enamel on an anodized aluminum plate.

- All buried valves shall be tagged with a brass plate cast into a 6-inch by 6 inch concrete pad at grade next to the valve box.  The valve number shall be engraved in the brass plate with lettering and numerals at least 1 inch high.

2.04  PANEL NAMEPLATES

- Nameplates shall be provided on the face of each panel and cabinet.  Panel identification nameplates shall be mounted at the top of the panel shall include the panel descriptive name and tag number as indicated on the drawings, in two or three lines of text.  Lettering shall be ¾ inch high.

- Nameplates for devices mounted on or in the panel shall be inscribed with the text as indicated on the Drawings.  Where nameplate information is not indicated on the drawings, inscriptions shall be in accordance with information in the supplier’s submittal drawings as guided by information in the relevant specification section.  Panel device nameplates shall have engraved letters 3/16 inch high.

- Nameplate material and size shall be as specified above for equipment number plates. Nameplates shall be secured to the panel with stainless steel pan head screws.

2.05 INSTRUMENT TAGS

- Temporary  Tags  - Where instruments are not provided with permanent tags furnished from the factory; instruments shall be tagged or marked in the factory with the instrument tag number indicated on the Drawings.

- Permanent  Tags -  Instruments shall be tagged with the instrument tag number indicated on the Drawings.  Tags shall be 12-gauge stainless steel with engraved or imprinted symbols.  Lettering on tags shall be ¼ inch high.  Tags shall be rectangular with smooth edges, and shall be fastened to the instrument with stainless steel mechanical fasteners or with a stainless steel chain.

PART 3 – EXECUTION

- All plates, tags, and nameplates addressed in Part 2 of this specification section shall be installed for Section 01 77 19 – Substantial Completion.

END OF SECTION