SECTION 01 75 01

EQUIPMENT FACTORY ACCEPTANCE TESTING

# GENERAL

## SECTION INCLUDES

### Scope.

### Submittals.

## RELATED SECTIONS

NOTE TO SPECIFIER:	Under item A below, a table of equipment to be started and checked is to be provided.  In addition, a disclaimer is required regarding startup and checkout activities not being all inclusive due to the fact that some requirements may be included elsewhere in the Contract Documents.

### Drawings and requirements of the contract as put forth in the various portions of the Project Manual, including General Conditions, any Special Provisions, and other Division 1 through Division XX Specification Sections and addenda apply to this Section.  A Partial list of specification sections where Equipment Factory Acceptance Testing are indicated as being required is presented for convenience in the table appearing below but this summary is not guaranteed to be all inclusive of all references and related sections for Equipment Factory Acceptance Testing that may appear elsewhere in the Contract Documents (Contractor’s attention to any addenda modifications is of particular importance).

| Title of Specification Section | Specification Reference Number | Comments |
| --- | --- | --- |

### Manufacturer Product Warranties are included in Section 0178 36.

### Contractor’s General Condition Warranty and Guarantee are included in the General Conditions, Section 00 72 00, Article 6.19.

### Commissioning Requirements and Sequence, Section 01 75 00.  (See PART 4 for the Commissioning Requirements and Sequence flow chart associated with this Section.)

### Equipment Startup and Checkout, Section 01 75 02.

### System Functional Testing, Section 01 75 03.

### Process Performance Testing, Section 01 75 04.

### Operational Testing, Section 01 75 05.

### 30-Day Commissioning Reliability Test, Section 01 75 06.

## SCOPE

### Equipment Factory Acceptance Testing ("FAT") shall be performed to verify proper assembly, per the manufacturer’s documentation and technical specifications.  Drawings by the CONTRACTOR are also reviewed to verify accuracy and completeness.

### Equipment FAT shall be performed by the CONTRACTOR.  At the CITY’s discretion, some or all Equipment FAT’s may be witnessed by the CITY.

### Equipment FAT shall be performed for all fully assembled control panels, cabinets, and other pertinent control systems and devices.  Equipment FAT also includes static and dynamic testing of wiring and devices, mechanical connections, and preliminary mechanical functionality, as required by the Contract Documents.

### Equipment FAT shall be performed at the location where the equipment or panel was assembled, immediately prior to shipment to the CITY’s facility.  Equipment FAT shall be initiated and performed by the CONTRACTOR after the equipment or system has been fabricated and assembled in the factory.  Prior to Equipment FAT, all mechanical connections shall have been completed, and all power and temporary wiring shall be terminated, as applicable.

### All Equipment FAT procedures and results shall be documented, indicating compliance with the manufacturer’s recommendations and the requirements of the Contract Documents.  The accuracy and completeness of the drawings and documentation shall also be verified and corrected as necessary.

### In accordance with Commissioning Requirements and Sequence, Section 01 75 00, Equipment FAT shall be successfully completed in compliance with Part 3 Execution and approved prior to execution of all subsequent verification sections, including Equipment Checkout and Startup, Section 01 75 02.

### Contractor shall submit FAT report documenting testing results including, but not limited to:

i.	Verification of all equipment with submitted Bill of Material (BOM).

ii.	I/O List checkoff

iii.	Functional test of protective devices including circuit breakers, fuses, etc.

iv..	Power supply voltage output

v.	UPS testing and holdup time with full load

vi.	Interposing and control relay functionality

vii.	Enclosure rating, UL label and serial number

viii.	All labeling, tagging and wire numbers match approved shop drawings

## SUBMITTALS

### Equipment FAT Plan.  The CONTRACTOR shall submit all of the following documents to the CITY for approval (referred to as the "Equipment FAT Plan").  Upon receipt of the CITY’s approval, the CONTRACTOR shall coordinate Equipment FAT activities with the CITY’s staff at least two (2) weeks prior to the proposed date Equipment FAT is to begin.

### Submittal Documents.

#### Proposed start day of Equipment FAT tasks to be performed, including testing procedures and what functionality or document detail is to be verified.

#### Examples of the forms to be used to document tasks, successful completion and deficiencies.

#### Detailed panel layout drawing, including itemized bill of materials.

#### Control panel schematic diagrams.

#### PLC input and output (I/O) drawings.

#### Controls sequences and functional descriptions.

#### Digital network diagrams and riser diagrams.

#### PLC source files. – Not applicable if Programming by Owner or Owner’s Engineer.

#### PLC documentation, complete, in PDF format, including all available aspects of the project report available within the PLC programming software. – Not applicable if Programming by Owner or Owner’s Engineer

#### HMI documentation, in PDF format, including a full-page screenshots of every overview and control screen, complete tag database, complete driver database and all custom programming scripts. – Not applicable if Programming by Owner or Owner’s Engineer

#### Mechanical assembly documentation and drawings.

#### FAT Test Report.

# PRODUCTS

# NOT USED

## EXECUTION

## PREPARATION

### At least three (3) work days prior to Equipment FAT activities and arrival of the CITY, the CONTRACTOR shall verify that the equipment is powered and ready for testing.  All installations shall be complete.  All temporary connections shall be made, and all electrical and mechanical aspects of each component and equipment are properly installed.  Electrical control power, uninterruptible power supplies, and reduced voltage power supplies shall be energized and verified.

### The CITY shall be notified immediately of any circumstances which may hinder, delay or interrupt the Equipment FAT.

### All test equipment and analysis instruments to be used for Equipment FAT verification shall be calibrated and prepared for testing.

## EXECUTION: EQUIPMENT FACTORY ACCEPTANCE TESTING

### Equipment FAT may begin two (2) weeks after approval of each applicable Equipment FAT Plan, subject to the following stipulations:

#### Refer to each applicable technical specification section for clarifications or additional installation and Equipment FAT requirements or expectations.

#### All Equipment FAT activities shall be coordinated with the CITY, at least two (2) weeks in advance.  At the CITY’s discretion, the CITY may elect to witness some or all of these activities.

#### Once started, Equipment FAT shall continue or be repeated until successful completion is accomplished.  All requests to interrupt, suspend, or restart Equipment FAT activities shall be submitted to CITY for approval.

#### Equipment FAT shall be successfully completed and approved prior to shipment, as well as Execution of all subsequent verification sections, including Equipment Checkout and Startup, Section 01 75 02.

### All details of all documents required for Submittal for this Section shall be verified.  Each word and marking on the documentation and drawings shall be visually inspected, functionally tested, and highlighted to indicate accuracy.

### Electrical Equipment FAT shall be performed, including the following, per the manufacturer’s documentation and the technical specifications:

#### With power off, verify each detail of each drawing for completeness and accuracy.  Verify that all panel equipment, components and wires are properly labeled and tagged.  Verify terminal and tag lists.  Verify physical layout and measurements.

#### Verify that the Bill of Materials adequately describes the equipment installed and that all equipment meets the requirements of the design and approved Submittal documents per each applicable technical section.

#### Record identification information of all parts with a Serial Number.

#### Verify that all installations of electrical equipment and conductors are per the manufacturer’s recommendations, especially regarding proper sizing, color coding, grounding, insulation, resistance and protection.

#### Verify wire routing and labels, including separation of AC and DC wiring.

#### Verify and record UL approval label identification.

#### With power applied, verify proper and functional circuit and motor protection equipment, such as disconnects, breakers, fuses and overloads.  Measure, verify and record the current through each protected device.

#### Verify the functionality of each panel device.

#### Verify all PLC modules match approved Bill of Material. Document hardware and firmware version of each module including CPU, communication, specialty and I/O modules.

#### Perform complete PLC I/O test using I/O listing developed from approved shop drawings.

##### Test Discrete Inputs by applying appropriate voltage at each input’s field terminal block. Observe LED status indicator and record results.

##### Test Discrete Outputs by forcing PLC output.  Observe LED light and confirm interposing relay, if used, is energized and verify relay contact output is on at field terminals.Test analog inputs by injecting a 4-20 mA signal at field terminals and verify in PLC data table.  Simulate 0, 25, 50, 75 and 100% (0, 4, 8, 12, 16 and 20mA),

##### Test analog outputs by setting output value in PLC data table and reading at field terminals.  Set output at 0. 25, 50, 75 and 100% and observe 0, 4, 8, 12, 16 and 20 mA signal at field terminals.

MSD will provide a PLC program for FAT testing for Contractor convenience if requested in writing.  The PLC program will be developed with project specific configured using MSD’s current preferred PLC CPU firmware version.  It will be the Contractor’s responsibility to load the required firmware version to PLC CPU to perform FAT.

The Contractor is responsible for providing PLC programming software for their use during testing.

### Instrument and Control Equipment FAT shall be performed, including the following, per the manufacturer’s documentation and the technical specifications:

Note: – Not applicable if Programming by Owner or Owner’s Engineer

#### Verify each point, one point at a time, applying the applicable voltage or current to each field input termination point.  Verify proper functionality of the hardware, software and HMI indication.  By making database adjustments, cause the proper signal to each field output termination, then measure and record.

#### Perform functional tests of each algorithm described in the Functional Description.  Use simulation software or test assembly to simulate field devices.

#### Make connections to each field termination as necessary to simulate each Control Sequence.  Verify all outputs, PLC programming and HMI configurations.

#### Verify correct operation of each HMI element, including navigation, graphics, numerical displays, controls, alarms and trends.

#### Verify program tag identifications, including PLC program and HMI configuration.

#### Perform fault tolerance (what-if) and failure recovery testing.

### Mechanical Equipment FAT shall be performed, including the following, per the manufacturer’s documentation and the technical specifications:

#### Verify that all equipment and components have been fully and properly installed.

#### Verify mechanical connections, fittings and mountings.

#### Verify equipment alignment.

#### Verify proper operation.

### If any Equipment FAT cannot be completed successfully, necessary modifications, adjustments, repairs or field engineering shall be performed as required for successful completion.  Equipment FAT shall continue or be repeated prior to submittal of any completed documentation for approval, until successful completion is accomplished.

### No equipment shall ship to the Project Site until all Equipment FAT is successfully completed and approved.

### Any proposed deviation from the approved plans or schedules shall require written authorization by the CITY.

## DOCUMENTATION

### Only the forms and documents submitted to and approved by CITY shall be used to document Equipment FAT.  As each activity is completed, all related forms shall be completed, dated and signed by the CONTRACTOR.

### The CONTRACTOR shall maintain a list of Equipment FAT deficiencies, which shall be updated and sent to the CITY at the end of each week during testing.  All deficiencies shall be corrected prior to submittal of any completed documentation for approval.

### Upon completion of all Equipment FAT, all completed and witnessed documents shall be compiled and formally submitted for approval.

PART 4 -	FLOW CHART

Refer to 01 75 00 Section 2 for the Equipment Factory Acceptance Testing workflow.

END OF SECTION 01 75 01