SECTION 01 75 02

EQUIPMENT STARTUP AND CHECKOUT

# PART 1 - GENERAL

## SECTION INCLUDES

### Scope.

### Submittals.

## RELATED SECTIONS

NOTE TO SPECIFIER:	Under item A below, a table of equipment to be started and checked is to be provided.  In addition, a disclaimer is required regarding startup and checkout activities not being all inclusive due to the fact that some requirements may be included elsewhere in the Contract Documents.

### Drawings and requirements of the contract as put forth in the various portions of the Project Manual, including General Conditions, any Special Provisions, and other Division 1 through Division XX Specification Sections and addenda apply to this Section.  A Partial list of specification sections where Equipment Startup and Checkout are indicated as being required is presented for convenience in the table appearing below but this summary is not guaranteed to be all inclusive of all references and related sections for Equipment Startup and Checkout that may appear elsewhere in the Contract Documents (Contractor’s attention to any addenda modifications is of particular importance).

| Title of Specification Section | Specification Reference Number | Comments |
| --- | --- | --- |

### Manufacturer Product Warranties are included in Section 01 78 36.

### Contractor’s General Condition Warranty and Guarantee are included in the General Conditions, Section 00 72 00, Article 6.19.

### Commissioning Requirements and Sequence, Section 01 75 00.  (See Part 4 for the Equipment Factory Acceptance Testing flow chart associated with this section.)

### Equipment Factory Acceptance Testing, Section 01 75 01.

### System Functional Testing, Section 01 75 03.Process Performance Testing, Section 01 75 04.

### Operational Testing, Section 01 75 05.

### 30-Day Commissioning Reliability Test, Section 01 75 06.

## SCOPE

### Equipment Startup shall be performed to verify proper installation and initial, powered operation of equipment.

### Equipment Startup shall be performed by the CONTRACTOR, as described by the manufacturer’s documentation and recommendations.  The services of factory field service representatives shall be utilized, as directed in the technical specifications or recommended by the manufacturer.  Refer to each applicable technical specification section for clarifications or additional installation and startup requirements or expectations.

### After installation is completed, components and equipment shall be initially powered.  Electrical power feeds and supplies currents shall be measured and recorded.  Rotating equipment shall be tested, especially regarding proper rotation direction, alignment and vibration.

### All Equipment Startup procedures and results shall be documented, showing compliance with the manufacturer’s recommendation, as well as the requirements of the technical specifications.

### All instrument and control signals shall be calibrated and verified for proper loop performance.  Instrument and control signals shall be simulated as necessary to test and verify equipment functionality.  All discrete signals shall be verified for proper activation and continuity.  All digital communications signals and devices shall be tested for proper operation.

### In accordance with Commissioning Requirements and Sequence, Section 01 75 00, Equipment Startup and Checkout Execution shall be initiated only subsequent to all successful Equipment Factory Acceptance Testing, Section 01 75 01.

### Equipment Startup shall be successfully completed in compliance with Part 3, Execution and approved prior to Execution of all subsequent verification sections, including Functional Testing, Section 01 75 03.

#### 1.04  	SUBMITTALS

### Equipment Startup Plan.  A set of detailed Equipment Startup Plans shall be submitted for approval.  Each Equipment Startup Plan shall be specific to the equipment or system to be tested.  Markups and excerpts of the manufacturer’s operation and maintenance manuals are acceptable.  Each Equipment Startup Plan shall include detailed documentation, as follows:

### Submittal Documents

#### A comprehensive list of the equipment or instruments to be factory calibrated, prior to delivery.

#### A comprehensive list of the equipment or instruments to be calibrated by a factory field service representative.

#### A comprehensive list of the equipment, instruments to be field calibrated by CONTRACTOR authorized personnel.

#### Copies of detailed Equipment Startup reports and calibrations completed, signed and dated by factory or factory authorized personnel who performed the Work.

#### A statement of qualifications for the CONTRACTOR personnel proposed to conduct field Equipment Startup and calibrations.  Documentation shall include experience and attendance in applicable training courses.

#### Copies of calibration forms to be used.  Forms shall be modified as necessary to reflect any additional measurements or requirements indicated by the manufacturer’s recommended calibration instructions.  Each form shall be preprinted to the extent possible prior to field startup and calibration.  Each calibration form shall indicate the maximum and minimum transmitted value, for each test point, required for successful calibration.

#### A list of test and support equipment, temporary systems and other resources required to complete Equipment Startup and calibrations.

#### Copies of certifications, which indicate the validity or recent calibration of all test equipment and resources to be used.

#### An outline of specific resources to be provided by the CITY, such as the isolation of systems or processes.

# PART 2 - PRODUCTS

# NOT USED

# PART 3 – EXECUTION: EQUIPMENT STARTUP AND CHECKOUT

# 3.01 	PREPARATION

### Prior to startup, all structural and mechanical aspects of each component and equipment shall be verified for complete and proper installation.  All permissive, interlocks and safety devices shall be verified to be in place and fully functional.

### The CONTRACTOR shall assure that all preliminary and cursory installation reviews have been performed and corrected, including inspections of connections, fittings and mountings.  All safeties, guards and interlocks shall be completed and placed in operation.

### Electrical distribution, control power, uninterruptible power supplies, and reduced voltage power supplies shall be energized, measured, verified and documented.

### All test equipment and analysis instruments to be used for Equipment Startup verification shall be calibrated and certified prior to testing.  At the CITY’s discretion, test equipment or analysis instruments may be subject to re-certification after completion of Equipment Startup.

### 3.02	EQUIPMENT STARTUP AND CHECKOUT

## A.	Equipment Startup may begin two (2) weeks after approval of each applicable Equipment Startup Plan, subject to the following stipulations:

#### The CONTRACTOR shall notify the CITY at least eight (8) work hours prior to each Equipment Startup or calibration activity.  To minimize facility disruptions, all Equipment Startup and calibration activities shall be coordinated with the CITY.  At the CITY’s discretion, the CITY may elect to witness some or all of these activities.

### Instrument calibrations shall be performed per the manufacturer’s instructions and the technical specifications.

### Equipment Startup or calibrations, which are not performed and documented by the factory or factory representative, shall be performed by the CONTRACTOR.  Equipment setup in a CONTRACTOR shop area shall be field verified after completion of permanent installation.  Field verification of transducers, meters, transmitters and analytical instruments shall be performed by applying sample process conditions to the sensor.  The use of factory authorized simulators may be used to simulate the sensing device.  Calibration procedures, which only test the output transmitted signal are not sufficient for successful completion of verification or calibration.

### Loop testing shall not commence until all individual component calibration has been successfully completed and documented.  Each instrument loop shall be tested as an integrated system.  This test shall verify proper operation from the sensing device or switch to all receiving components within the loop.  For loop testing, signals may be injected at the signal connection to the primary measuring elements.  Loop testing, which includes an interface to a programmable logic controller (PLC), shall include verification of the PLC processor, the input/output (I/O) database and the I/O system.  If any loop device fails to operate or indicate properly, corrections shall be made, and the loop test repeated until all devices operate properly.  All loop tests shall be fully documented.

### Record the identification information of each field device, including Model No. and Serial Number.  Verify that all installed field devices are per the requirements of the design and approved submittal documents.

### Verify each point, one point at a time, applying the applicable voltage or current to each field input termination point.  Verify proper functionality of the hardware, software and HMI indication.  By making database adjustments, cause the proper signal to each field output termination, then measure and record.

### Verify network and communications documentation, including parts inventories, labels, cable terminations and testing certifications.  All equipment configuration parameters and addresses shall be set and recorded.

### Make connections to each field termination as necessary to simulate each Control Sequence and Functional Description.  Verify all outputs, PLC programming and HMI configurations.

### If any Equipment Startup or calibration is not completed successfully, necessary modifications, adjustments, repairs or field engineering shall be performed as required for successful completion.  Equipment Startup shall continue or be repeated until successful completion is accomplished.

### At the discretion of the CITY, previously completed calibrations shall be repeated if subsequent modifications may have altered the equipment or system, and to have logically affected previous test results or observations.

### Any proposed deviation from the approved plans or schedules shall require written authorization by the CITY.

## 3.03 	DOCUMENTATION

### Only forms submitted and approved shall be used during field Equipment Startup or calibration.  As each activity is completed, all forms shall be completed, dated and signed by the CONTRACTOR.

### The CONTRACTOR shall maintain a list of Equipment Startup or calibration deficiencies, which shall be updated and sent to the CITY at the end of each week.  All deficiencies shall be corrected prior to submittal of any forms for approval.

### Upon completion of all Equipment Startup and calibrations, all completed and witnessed documents shall be compiled and formally submitted for approval.

### The Contractor is responsible for developing and completing approved test report documentation during testing.

PART 4 – FLOW CHART

Refer to 01 75 00 Section 2 for the Equipment Startup and Checkout workflow.

END OF SECTION 01 75 02

THIS PAGE LEFT BLANK INTENTIONALLY