SECTION 01 75 03

SYSTEM FUNCTIONAL TESTING

# PART 1 - GENERAL

## SECTION INCLUDES

### Scope.

### Definitions

### Submittals.

## RELATED SECTIONS

NOTE TO SPECIFIER:	Under item A below, a table of equipment to be started and checked is to be provided.  In addition, a disclaimer is required regarding startup and checkout activities not being all inclusive due to the fact that some requirements may be included elsewhere in the Contract Documents.

### Drawings and requirements of the contract as put forth in the various portions of the Project Manual, including General Conditions, any Special Provisions, and other Division 1 through Division XX Specification Sections and addenda apply to this Section.  A Partial list of specification sections where System Functional Testing are indicated as being required is presented for convenience in the table appearing below but this summary is not guaranteed to be all inclusive of all references and related sections for System Functional Testing that may appear elsewhere in the Contract Documents (Contractor’s attention to any addenda modifications is of particular importance).

| Title of Specification Section | Specification Reference Number | Comments |
| --- | --- | --- |

### Drawings and general provisions of the contract, including General Conditions, Special Provisions, and other Division 1 Specification Sections apply to this Section.

### Manufacturer Product Warranties are included in Section 0178 36.

### Contractor’s General Condition Warranty and Guarantee are included in the General Conditions, Section 00 72 00, Article 6.19.

### Commissioning Requirements and Sequence, Section 01 75 00.  (See Part 4 for the Commissioning Requirements and Sequence flow chart associated with this Section.)

### Equipment Factory Acceptance Testing, Section 01 75 01.

### Equipment Startup and Checkout, Section 01 75 02.

### Process Performance Testing, Section 01 75 04.

### Operational Testing, Section 01 75 05.

### 30-Day Commissioning Reliability Test, Section 01 75 06.

## SCOPE

### Functional Testing shall be performed to verify proper powered operation of systems, comprised of multiple equipment and components ("Systems"), typically prior to exposing these to operating processes or conditions.

### Functional Testing shall be performed by the CONTRACTOR, and witnessed by the CITY, to verify proper integration, interaction and operation of component equipment, operating as a system, as described by the manufacturer’s documentation and recommendations.  Refer to each appropriate technical specification section for clarifications or additional functional requirements or expectations.  Functional Testing shall also include preliminary verification of each Functional Description, typically limited to dry testing.

### Basic System operation and control System response shall be tested and verified.  Instrument and control signals shall be simulated as necessary to test and verify all equipment functionality within the System.

### A System may be obtained from a single vendor.  Factory certified field service representatives or technicians shall be utilized for Functional Testing of each single source System.  Single source Systems are identified as such in the technical specifications included in the Contract Documents.

### Each System comprised of equipment and components from multiple vendors shall be assembled, integrated and functionally tested by the CONTRACTOR.

### For each System, the CONTRACTOR shall plan, schedule, execute and document the Functional Testing of the applicable and related System.

### In accordance with Commissioning Requirements and Sequence, Section 01 75 00, Functional Testing shall be initiated subsequent to all successful Equipment Start-Up, and Checkout, Section 01 75 02.

### System Functional Testing shall be successfully completed in compliance with Part 3, Execution and approved prior to Execution of all subsequent verification sections, including Process Performance Testing, Section 01 75 04.

## DEFINITIONS

### Successful Completion.  All aspects of Functional Testing have been completed, and all requirements listed in the specifications and in the Submittals have been proven to have been met, within the specified constraints.

### System.  Regarding Functional Testing, a System shall include all components of equipment, devices and appurtenances connected such that the operation or function of each complements, protects or controls the operation or function of the others.  For example, a pumping system may be comprised of various equipment: motor, pump, gear reducer, piping, instruments, controls, motor starter, wiring, etc.  Other examples of Systems used in wastewater facilities include power distribution, programmable controller, compressor, odor control, centrifuge or boiler.

## SUBMITTALS

### Functional Testing Plan.  A set of detailed Functional Testing Plans shall be submitted for approval.  The System Functional Testing may begin two (2) weeks after approval by the City.  Each Functional Testing Plan shall be specific to the equipment or System to be tested.  Markups and excerpts of the manufacturer’s operation and maintenance manuals are acceptable.  Each Functional Testing Plan shall include detailed descriptions of the preparation, execution and documentation, as follows:

#### A detailed list of the equipment and Systems to which the Functional Testing procedures will apply.  This list shall include at least all applicable mechanical, electrical, instrument, controls and HVAC equipment and Systems.

#### Complete descriptions of the preparation procedures necessary to achieve the desired test conditions.  Identify which items will require CITY action or participation.

#### A detailed list of procedures by which the CONTRACTOR plans to adequately and completely perform each aspect of the Functional Testing.

#### A list of test and support equipment, temporary systems and other resources required to complete the test plan.

#### A list of personnel, which will be used to perform Functional Testing.  This list shall indicate all subcontractors or representatives of manufacturers or vendors required to be present for testing.  At the CITY’s discretion, the qualifications of personnel shall be documented and provided for approval upon request.

#### An outline of specific resources to be provided by the CITY during testing, such as the isolation of systems or processes.

#### Verification of the validity or calibration of the test equipment or resources to be used.

#### A detailed outline of the specific results or observations, which will constitute acceptable completion of each Functional Testing Plan.

#### Sample documentation to be used to record the procedures and results of each Functional Testing Plan, including a sample of each form to be used.  Samples of the format and level of detail required for the documentation forms are available in Section 01 33 19

### Functional Testing Schedule.  A detailed Functional Testing Schedule shall be submitted for approval.  This Submittal shall accompany the Functional Testing Plan Submittal.  Requirements of the Functional Testing Schedule are as follows:

#### 1.	The proposed date that Functional Testing is to begin, and the estimated completion date.

#### 2.	A sequence, and relative daily schedule, by which the Functional Testing will be executed.

#### 3.	The proposed Functional Test dates shall be indicated on and coordinated with the CONTRACTOR’s Construction Progress Schedule specified in Section 01 32 16.

### Functional Testing Documentation and Results.  Upon completion of all aspects of Functional Testing, all documentation indicating compliance with the requirements shall be signed and dated by the CONTRACTOR for completeness and accuracy, and by the CITY as witness.  A copy of the project specific signed results shall be submitted to the CITY for consideration of successful completion.  Only upon approval of completion, by OWNER, shall the CONTRACTOR begin the Execution phase of subsequent verification Sections.

# PART 2 - PRODUCTS

# NOT USED

# PART 3 – EXECUTION:  SYSTEM FUNCTIONAL TESTING

## PREPARATION

### The CONTRACTOR shall inform and coordinate the activities of all individuals required for Functional Testing, including all subcontractors, vendors, suppliers, the CITY’s operations and maintenance personnel, and other resources needed to implement the requirements of this section.

### The CONTRACTOR shall assure that all preliminary and cursory installation reviews have been performed and mitigated, including inspections of connections, fittings, mountings, leaks, pressures, temperatures, vibrations, electrical measurements, rotations and alarms.  The testing areas shall be cleaned and free of installation equipment and debris.  All safeties, guards and interlocks shall be completed and placed for operation.

### All test equipment and analysis instruments to be used for Functional Testing shall be calibrated and certified prior to Functional Testing.  At the CITY’s discretion, test equipment or analysis instruments may be subject to re-verification after completion of the Functional Testing and prior to approval.

## SCHEDULE

### The approved Functional Testing Schedule shall be followed.

### The schedule shall be updated and posted weekly, showing actual dates of test Work, and indicating the status of each Functional Testing Plan.  Functional Testing procedures and Schedules shall be contiguous for each System, only interrupted for necessary modifications, adjustments, repairs and field engineering, as required for successful completion.  If any interruption exceeds two (2) hours, the CONTRACTOR shall give twenty four (24) hours notice to the CITY and all resources, prior to continuation or restart of the Functional Testing Plan.

## FUNCTIONAL TESTING

### Functional Testing shall proceed under the direction of the CONTRACTOR.  Only one System and Functional Test Plan shall be executed at a time.  All Functional Testing shall follow the approved Plans and Schedules. Functional testing shall be executed with participation of MSD or MSD’s Consultant.  The Contractor is responsible for testing and verifying all equipment and instruments supplied by the Contractor.  The MSD or MSD’s Consultant shall facilitate testing from PLC/HMI and verify proper feedback from field devices to PLC/HMI.

### If any Functional Testing Plan is not completed successfully, necessary modifications, adjustments, repairs or field engineering shall be performed as required for successful completion.  Functional Testing shall continue or be repeated until successful completion is accomplished.

### Verify each point, one point at a time, applying the applicable voltage or current to each field input termination point.  Verify proper functionality of the hardware, software and HMI indication.  By making database adjustments, cause the proper signal to each field output termination, then measure and record.  All equipment configuration parameters and addresses shall be set and recorded.

### At the discretion of the CITY, previously completed Functional Test Plans shall be repeated if subsequent modifications may have altered the equipment or System, and to have logically affected previous test results or observations.

### Any proposed deviation from the approved Functional Testing Plans or Schedules shall require written authorization by the CITY.

## DOCUMENTATION

### As each procedure is completed, the results shall be documented, dated and signed by the CONTRACTOR.  The CITY will also sign and date the documentation as witness.

### The CONTRACTOR shall maintain a list of Functional Deficiencies, which shall be updated and sent to the CITY at the end of each week.

### Upon completion of all Functional Testing, all completed and witnessed documents shall be compiled and formally submitted to the CITY for approval.

### The Contractor is responsible for developing and completing approved test report documentation during testing.

## PROGRESS PAYMENTS

### As a condition precedent to receiving progress payments in the period in advance of the date the CONTRACTOR wishes to begin any testing work, the CONTRACTOR must have had submitted all Functional Testing Plans required for the systematic field performance and operational tests for all equipment and Systems installed under the Contract Documents.  Once the CITY has reviewed and taken no exception to the CONTRACTOR’s Functional Testing Plans, the CONTRACTOR shall reproduce the Functional Testing Plans in sufficient number for the CONTRACTOR’s purposes and an additional five (5) copies for delivery to the CITY.  No Functional Testing work shall begin until the CONTRACTOR has delivered the specified number of approved Functional Testing Plans to the CITY.

PART 4 – FLOW CHART

Refer to 01 75 00 Section 2 for the System Functional Testing workflow.

END OF SECTION 01 75 03