SECTION 01 75 04

PROCESS PERFORMANCE TESTING

NOTE TO SPECIFIER: The Process Performance Testing specification section (01 75 04) is for testing a process (equipment or system) when the process is initially exposed to the actual operating media and conditions or to a surrogate media and conditions if using the operating media is not practical.  The testing is performed to verify that the equipment and systems are operating properly without a focus on meeting specified operational parameters.

# PART 1 - GENERAL

## SECTION INCLUDES

### Scope.

### Definitions.

### Submittals.

## 1.02     RELATED SECTIONS

NOTE TO SPECIFIER:	Under item A below, a table of equipment to be started and checked is to be provided.  In addition, a disclaimer is required regarding startup and checkout activities not being all inclusive due to the fact that some requirements may be included elsewhere in the Contract Documents.

    - Drawings and requirements of the contract as put forth in the various portions of the Project Manual, including General Conditions, any Special Provisions, and other Division 1 through Division XX Specification Sections and addenda apply to this Section.  A Partial list of specification sections where Process Performance Testing are indicated as being required is presented for convenience in the table appearing below but this summary is not guaranteed to be all inclusive of all references and related sections for Process Performance Testing that may appear elsewhere in the Contract Documents (Contractor’s attention to any addenda modifications is of particular importance).

| Title of Specification Section | Specification Reference Number | Comments |
| --- | --- | --- |

### B.  Drawings and general provisions of the contract, including General Conditions, Special Provisions, and other Division 1 Specification Sections apply to this Section.

### C.  Manufacturer Product Warranties are included in Section 01 78 36.

### Contractor’s General Condition Warranty and Guarantee are included in the General Conditions, Section 00 72 00, Article 6.19.

### Commissioning Requirements and Sequence, Section 01 75 00.  (See Part 4 for the Process Performance Testing flow chart associated with this Section.)

### Equipment Factory Acceptance Testing, Section 01 75 01.

### Equipment Startup and Checkout, Section 01 75 02.

### System Functional Testing, Section 01 75 03.

### Operational Testing, Section 01 75 05.

### 30-Day Commissioning Reliability Test, Section 01 75 06.

## SCOPE

### Process Performance Testing shall be performed to verify proper powered operation of equipment and Systems, as intended to perform a Process.

### Performance Testing is performed as the process is initially exposed to operating or surrogate media and conditions.

### Performance Testing shall be performed by the CONTRACTOR to verify proper operation, as described by the following items, as outlined in the technical specifications in the Contract Documents.  Refer to each appropriate technical Specification Section for the performance requirements or expectations.  Performance requirements may be specified for various media conditions and levels of operation, including equipment, System and Process.

#### Specific performance parameters or expectations.

#### The Functional Description, complete.

#### The Sequence of Operation.

#### Alternative modes of operation.

#### Process functionality, using process or surrogate media as practical.

#### Process or System upsets and recovery:

#### NOTE TO SPECIFIER:  A table of processes and systems with specific items to be tested in terms of upsets and recovery is to be provided.  In addition, a disclaimer is required regarding upsets and recovery not being all inclusive due to the fact that some requirements may be included elsewhere in the Contract Documents.

### For each of the items listed, the CONTRACTOR shall plan, schedule, execute and document the Performance Testing of the applicable and related equipment, Systems and Processes.

### In accordance with Section 01 75 00, Commissioning Requirements and Sequence, Performance Testing shall be initiated subsequent to the approved Successful Completion of Functional Testing, Section 01 75 03.

### Performance Testing shall be performed by the CONTRACTOR, and witnessed by the CITY.  If specifically required by a technical specification included in the Contract Documents, or otherwise at the CITY’s discretion, Certified Performance Tests may be required in lieu of an CITY-Witnessed Performance Test.

### The CONTRACTOR shall identify and utilize the services of a Testing Manager, to oversee and directly supervise all aspects pertaining to Performance Testing and Operational Testing.

### Performance Testing shall be successfully completed in compliance with Part 3, Execution and approved prior to Execution of all subsequent verification sections, including Operational Testing, Section 01 75 05.

## DEFINITIONS

### Successful Completion.  All aspects of Performance Testing have been completed, and all requirements listed in the specifications and in the submittals have been proven to have been met, within the specified constraints.

### Testing Manager.  The person appointed by the CONTRACTOR to plan, schedule, manage, coordinate, and supervise the CONTRACTOR’s Performance Testing and Operational Testing programs, including Submittals, Execution and Documentation.

### Certified Performance Testing.  Tests performed and documented by factory authorized personnel.

### System.  Regarding Performance Testing, a System shall include all items of equipment, devices and appurtenances connected such that the operation or function of each complements, protects or controls the operation or function of the others.  The following are examples of systems used in wastewater facilities: pumping, flow measurement, programmable controller, level controls, compressor, centrifuge and boiler.

### Process.  Regarding Performance Testing, a Process shall include a collection or series of Systems or equipment, which act together upon a fluid media to cause a separation or change in properties, location or energy.  The following are examples of wastewater processes: grit removal, clarification, aeration, dewatering and incineration.

## SUBMITTALS

### Testing Manager.  The CONTRACTOR shall propose the appointment of a Testing Manager to execute the CONTRACTOR’s Performance Testing and Operational Testing programs.  Upon approval, the Testing Manager shall also develop all subsequent Submittals required by the Performance Testing and Operational Testing Specification Sections.  The Testing Manager Submittal shall include detailed descriptions of the proposed Testing Manager’s qualifications and experience in executing, managing and coordinating similar Performance and Operational Testing programs.  An Operations Engineer or equally qualified Operations Specialist, is expected.  Operations Engineers shall be graduates of a minimum 4-year curriculum in mechanical, civil or equivalent engineering discipline.  Operations Specialists shall have relevant qualifications and experience in plant process operation and maintenance activities.  The submittal pertaining to the Testing Manager shall be approved by CITY prior to the Testing Manager’s development of all subsequent Submittals in the Performance Testing section.

### Performance Testing Plan.  A set of detailed Performance Testing Plans shall be submitted to CITY for approval.  The complete Performance Testing Plans shall be submitted no later than two (2) weeks in advance of the proposed date testing is to begin.  Each Performance Testing Plan shall be specific to the equipment or System to be tested.  Each Performance Testing Plan shall include detailed descriptions of the preparation, execution and documentation, as follows:

#### A detailed list of the equipment, systems and processes to which the Performance Testing procedures will apply.  This list shall include at least all applicable mechanical, electrical, instrument, controls, HVAC and process equipment and systems.  It shall be indicated whether a Certified Performance Test or a CITY-Witnessed Performance Test is to be performed for each equipment, System or Process.

#### Copies of all Functional Descriptions, Alternative Modes of Operation, Sequence of Operations, and Outline of System Upsets and Recovery to be tested, simulated and verified by the Performance Testing.

#### Complete descriptions of the preparation procedures necessary to achieve the desired test conditions.

#### A detailed list of procedures by which the CONTRACTOR plans to adequately and completely perform each aspect of the Performance Testing.  The compiled list of the Performance Testing procedures shall address all components of all descriptions - Functional Description, Mode of Operation, Sequence of Operations or System Upset and Recovery.

#### A list of test and support equipment, temporary systems and other resources required to complete the test plan.

#### A list of personnel, which will be used to perform Performance Testing.  This list shall indicate all subcontractors or representatives of manufacturers or vendors required to be present for testing.  At the CITY’s discretion, the qualifications of personnel shall be documented and provided upon request.

#### An outline of specific resources to be provided by the CITY, such as the isolation of systems or processes.

#### Verification of the validity or calibration of the test equipment or resources to be used.

#### A detailed outline of the specific results or observations, which will constitute successful completion of each Performance Testing plan.

#### Sample documentation to be used to record the procedures and results of each Performance Testing plan, including a sample of each form to be used.  Samples of the format and level of detail required for the documentation forms are available in Section 01 33 19

### Performance Testing Schedule.  A detailed Performance Testing Schedule shall be submitted for approval.  This submittal shall accompany the Performance Testing Plan submittal.  Requirements of the schedule are as follows:

#### 1.	The proposed date that Performance Testing is to begin, and the estimated completion date.

#### 2.	A sequence, and relative daily schedule, by which the Performance Testing will be executed.

#### 3.	The proposed Performance Test dates shall be indicated on and coordinated with the CONTRACTOR’s Construction Progress Schedule specified in Section 01 32 16.

### Performance Testing Documentation and Results.  Upon completion of all aspects of Performance Testing, all documentation indicating compliance with the requirements shall be signed and dated by the Testing Manager for completeness and accuracy, and by the CITY as witness.  A copy of the signed results shall be submitted to the CITY for consideration of Successful Completion.  Only upon approval of this Submittal shall the Contractor begin to execute subsequent verification Sections.

### For items requiring only Certified Performance Testing, documentation of this certification shall be submitted to the CITY for approval.

# PART 2 - PRODUCTS

# NOT USED

# PART 3 – EXECUTION:  PROCESS PERFORMANCE TESTING

## 3.01 	PREPARATION

### The Testing Manager shall inform and coordinate the activities of all individuals required for Performance Testing, including the CONTRACTOR, all subcontractors, vendors, suppliers, the CITY’s operations and maintenance personnel, and other resources needed to implement the requirements of this section.

### The Testing Manager shall assure that all preliminary and cursory installation reviews have been performed and mitigated, including inspections of connections, fittings, mountings, leaks, pressures, temperatures, vibrations, electrical measurements, rotations and alarms.  The testing areas shall be cleaned and free of installation equipment and debris.  All safeties, guards and interlocks shall be completed and placed for operation.  All temporary equipment and configurations, including bypasses and jumpers, shall no longer be required and shall be removed.

### All test equipment and analysis instruments to be used for Performance Testing shall be available.  At the CITY’s discretion, test equipment or analysis instruments may be subject to re-verification after completion of the Performance Testing.

## SCHEDULE

### The approved Performance Testing Schedule shall be followed.

### The schedule shall be updated and posted weekly, showing actual dates of testing, and the status of each test plan.  Performance Testing procedures and schedules shall be contiguous, only interrupted for necessary modifications, adjustments, repairs and field engineering, as required for successful completion.  If any interruption exceeds 4-hours, the Testing Manager shall provide at least twenty four (24) hours notice to the CITY and all resources, prior to continuation or restart of the test plan.

## PERFORMANCE TESTING

### Performance Testing shall proceed under the direction of the Testing Manager.  Only one process and one Performance Test plan shall be executed at a time.  All Performance Testing shall follow the approved plans and schedules.

### If any test plan is not completed successfully, necessary modifications, adjustments, repairs or field engineering shall be performed as required for successful completion.  Performance Testing shall continue or be repeated until successful completion is accomplished.

### At the discretion of the CITY, previously completed Performance Test plans shall be repeated if subsequent modifications may have altered the equipment, system or process, and to have logically affected previous test results or observations.

### Any proposed deviation from the approved plans or schedules shall require written authorization by the CITY.

## DOCUMENTATION

### As each procedure is completed, the results shall be documented, dated and signed by the Testing Manager.  The CITY will also sign and date the documentation as witness.

### The CONTRACTOR shall maintain a list of Performance Testing Deficiencies, which shall be updated and sent to the CITY at the end of each week.

### Upon completion of all Performance Testing, all completed and witnessed documents shall be compiled and formally submitted for approval.  Unless a waiver is granted in writing by the CITY, partial submittals of individual equipment, systems or processes shall not be submitted for review or considered for approval.

## PROGRESS PAYMENTS

### As a condition precedent to receiving progress payments in the payment period in advance of the date the CONTRACTOR wishes to begin any testing work, the CONTRACTOR must have had submitted all test plans required for the systematic field Performance Testing for all equipment and Systems installed under the Contract Documents.  Once the CITY has reviewed and taken no exception to the CONTRACTOR’s test plans, the CONTRACTOR shall reproduce the plans in sufficient number for the CONTRACTOR’s purposes and an additional five (5) copies for delivery to the CITY.  No test work shall begin until the CONTRACTOR has delivered the specified number of final test plans to the CITY.

PART 4 – FLOW CHART

Refer to 01 75 00 Section 2 for the Process Performance Testing workflow.

END OF SECTION 01 75 04