SECTION 01 75 06

30-DAY COMMISSIONING RELIABILITY TEST

NOTE TO SPECIFIER: Use of this specification may be impacted with projects that rely on wet weather events to perform reliability testing.

# GENERAL

## SECTION INCLUDES

### Scope.

### Submittals.

### Quality Assurance.

## RELATED SECTIONS

NOTE TO SPECIFIER:	Under item A below, a table of equipment to be started and checked is to be provided.  In addition, a disclaimer is required regarding startup and checkout activities not being all inclusive due to the fact that some requirements may be included elsewhere in the Contract Documents.

### Drawings and requirements of the contract as put forth in the various portions of the Project Manual, including General Conditions, any Special Provisions, and other Division 1 through Division XX Specification Sections and addenda apply to this Section.  A Partial list of specification sections where 30-Day Commissioning Reliability Testing are indicated as being required is presented for convenience in the table appearing below but this summary is not guaranteed to be all inclusive of all references and related sections for 30-Day Commissioning Reliability Testing that may appear elsewhere in the Contract Documents (Contractor’s attention to any addenda modifications is of particular importance).

| Title of Specification Section | Specification Reference Number | Comments |
| --- | --- | --- |

### B.  Drawings and general provisions of the contract, including General Conditions, Special Provisions, and other Division 1 Specification Sections apply to this Section.

### C.  Manufacturer Product Warranties are included in Section 01 78 36.

### Contractor’s General Condition Warranty and Guarantee are included in the General Conditions, Section 00 72 00, Article 6.19.

### Commissioning Requirements and Sequence, Section 01 75 00.  (See Part 4 for the 30-Day Commissioning Reliability Test flow chart associated with this Section.)

### Equipment Factory Acceptance Testing, Section 01 75 01.

### Equipment Startup and Checkout, Section 01 75 02.

### System Functional Testing, Section 01 75 03.

### Process Performance Testing, Section 01 75 04.

### Operational Testing, Section 01 75 05.

K. Substantial Completion, Section 01 77 19

## SCOPE

### This section contains requirements for the CONTRACTOR’s performance during the commissioning of the structures, equipment and systems constructed and installed during the course of the Work required by the Contract Documents.  All commissioning work, as described in this Section, shall be performed by the CONTRACTOR.

#### The commissioning process does not automatically begin solely upon completion of prior requirements as described in Section 01 75 00, but depends also on establishing normal operating parameters and completing other Work as described herein.

### Commissioning shall be performed to verify proper onsite installation, per the manufacturer’s documentation and technical specifications included in the Contract Documents.  Drawings by the CONTRACTOR are also reviewed to verify drawing accuracy and completeness.

### Equipment Commissioning shall be performed by the CONTRACTOR and witnessed by the CITY.  Depending upon the project, the City shall be responsible for the operation of the plant as related to obtaining the required effluent quality, controlling odor stack emissions and/or maintaining acceptable sound control decibel readings.

### Commissioning shall also include static testing of wiring and devices, mechanical connections, and preliminary mounting inspections.

### Commissioning shall be initiated and performed after all mechanical and electrical equipment have been delivered and fully installed.  Prior to Commissioning, all mechanical connections shall have been completed, and all power and interconnecting wiring shall be terminated and labeled.

### All Equipment Startup and Checkout procedures and results shall be documented, indicating compliance with the manufacturer’s recommendations and the requirements of the technical specifications included in the Contract Documents.  The accuracy and completeness of the drawings and documentation shall also be verified.

### All required training must be completed prior to the start of the 30-Day Commissioning Reliability Test.

### In accordance with the requirements of Commissioning Requirements and Sequence, Section 01 75 00, the procedure in the Execution section of the 30-Day Commissioning Reliability Test Specification shall be initiated only subsequent to all prior work being approved.

## SUBMITTALS

### All Shop Drawings and Operations and Maintenance Manuals are submitted in advance of the Commissioning Plan submittal.

### Commissioning Plan.  The CONTRACTOR shall submit all of the following documents listed to the CITY for approval (collectively referred to as the “Commissioning Plan”.  Upon receipt of the CITY’s approval of these documents, the CONTRACTOR shall coordinate the activities with the CITY’s staff and start the field 30-Day Commissioning Reliability Testing no sooner than two (2) weeks.

### Submittal Documents: the following information shall be submitted to the CITY in accordance within the provisions of Submittals, Section 01 33 00 and shall be field verified prior to submission:

#### Written verification that all installation tasks of the equipment to be included in the Equipment Commissioning activities have been totally completed, per the requirements of the design and approved Submittal documents.  This document shall also indicate that all permanent field equipment labels and tags are installed.

#### Motor Control Center wiring diagrams, marked and updated to identify field wiring connections and final circuit breaker assignments.

#### Control panel schematic diagrams, updated to include field wiring identification.

#### PLC input and output (I/O) drawings, updated to include field wiring identification.

#### Control panel interconnection diagrams, updated to include all field wiring.

#### Process and Instrument Diagrams (P&ID’s), updated to reflect any changes or clarifications made during installation.

#### Instrument loop diagrams, updated to include specific terminal and wire label identifications.

#### Digital network diagrams and riser diagrams, updated to reflect all device identification and cable labels.

#### A detailed certification procedure for verification of all digital network cables, including testing under static and dynamic conditions.

#### The CONTRACTOR’s plan for providing a Commissioning Team during the commissioning period.  The plan shall be complete with a daytime staffing plan and names, qualifications, and telephone numbers of those assigned to off-hour standby duty.

#### A schedule and subsequent updates, presenting the CONTRACTOR’s plan for commissioning systems installed under the Contract Documents.  The schedule shall establish the expected time period (calendar dates) when the CONTRACTOR plans to commence commissioning of the completed equipment and systems.  The schedule shall coincide with the CONTRACTOR’s Construction Progress schedule required in Section 01 32 16.

## QUALITY ASSURANCE

- CLEANUP: Following completion of the operational testing period, the CONTRACTOR shall remove, clean, and replace all permanent and temporary filters and strainers in all pipeline systems; replace all HVAC filters; dewater and clean all sumps; and dewater all process units for final inspection as a condition precedent to commissioning.

- COMMISSIONING TEAM:  The CONTRACTOR shall assemble a commissioning team under the direction of the Quality Assurance Manager. The CONTRACTOR shall appoint an operations engineer or equally qualified operations specialist as the Quality Assurance Manager to manage, coordinate, and supervise the CONTRACTOR’s quality assurance program. The Quality Assurance Manager shall be duly authorized to commit the CONTRACTOR’s personnel and resources to respond to requests for assistance on the part of the CITY.  The commissioning team shall consist of representatives of the CONTRACTOR’s mechanical, electrical, and instrumentation subcontractors, and others as appropriate (the "Commissioning Team").  The Commissioning Team shall be available at the site of the work during normal working hours (8 hours a day, 5 days a week, Saturdays, Sundays, and legal holidays excepted) and shall be available within two (2) hour’s notice at all other times upon notice by telephone.  The Commissioning Team shall at all times be equipped and ready to provide for emergency repairs, adjustments, and corrections to the equipment and systems installed and modified as a part of the Contract Documents.

# PRODUCTS

  - GENERAL (delete section 2.01 if designer is not scoped to prepare the O&M plan)

### Working with representatives of the CITY, the CONSULTANT shall develop and produce a detailed, written plan for operation, under actual operating conditions and actual process fluids and materials, of the equipment and systems installed and constructed under the Contract Documents.  The written plan for operation document, after acceptance by the CITY, shall serve as the CONTRACTOR’S guidance manual for the commissioning process and procedures.

## EXECUTION:  30-DAY COMMISSIONING RELIABILITY TEST

## PREPARATION

### Prior to Commissioning Execution, all structural and mechanical aspects of each component and equipment shall be verified for complete and proper installation.  All permissive, interlocks and safety devices shall be verified to be in place and fully functional.

### Commissioning shall commence only after all normal operating process parameters are established, including flow, pressure, temperature, etc., and all ancillary equipment is completely installed, calibrated and available for routine use.  Commissioning will be authorized only with written notice from the CITY that the equipment and systems did meet all test requirements and that commissioning may proceed.  The commissioning period for each modified or new major equipment or new unit process system shall be a minimum of thirty (30) days.  The CONTRACTOR shall remove all temporary appurtenances and other alterations to the permanent systems that may have been needed during the performance and operational testing and shall perform the tasks necessary to make the improvements constructed under the Contract Documents fully operational.  The CONTRACTOR shall complete all punch list items designated by the CITY as necessary for commissioning prior to beginning the commissioning period.

### The CONTRACTOR shall assure that all preliminary and cursory installation reviews have been performed and corrected, including inspections of connections, fittings and mountings.  All safeties, guards and interlocks shall be completed and placed in operation.

### The CONTRACTOR shall be available at all times during commissioning periods to provide immediate assistance in case of failure of any portion of the equipment or system being constructed.  At the end of the commissioning period and when all corrections required by the CITY to assure a reliable and completely operational facility are complete, the CITY shall issue a commissioning reliability test completion certificate, which is a prerequisite for Substantial Completion.  All equipment and each system shall have been issued a test completion certificate as a condition precedent to the  Substantial Completion of the Work under the Contract Documents.

### Proper installation of electrical equipment and conductors shall be verified per the manufacturer’s recommendations, especially regarding proper sizing, grounding, insulation, resistance and protection.

### All test equipment and analysis instruments to be used for Commissioning verification shall be calibrated and certified prior to testing.  At the CITY’s discretion, test equipment or analysis instruments may be subject to re-certification after completion of Commissioning.

### Refer to each applicable technical specification section in the Contract Documents for clarifications or additional installation and commissioning requirements or expectations.

### Electrical Equipment Commissioning shall be performed, including the following, per the manufacturer’s documentation and the technical specifications:

#### Check and correct all items used during installation to temporarily defeat the designed operation of equipment and systems, including undocumented jumpers and non-terminated wires.

#### Verify field equipment labels and tags, including the identification of the breaker, from which each device is fed.

#### Verify proper and functional circuit and motor protection equipment, such as disconnects, breakers, fuses and overloads.

#### Verify that all installations of electrical equipment and conductors are per the manufacturer’s recommendations, especially regarding proper sizing, grounding, insulation, resistance and protection.

#### Verify proper and functional personnel protection equipment, such as disconnect handles, lockout devices, machine guards, safety protection & emergency stop switches, gas detectors, and signaling devices.  Verify that all protection devices are in place and enabled.

### Instrument and Controls Equipment Commissioning shall be performed, including the following, per the manufacturer’s documentation and the technical specifications:

#### Verify all field wire terminations, per I/O drawings and interconnect drawings.  Drawings shall be updated to include specific terminal identification.

#### Verify wire routing and labels, including separation of AC and DC wiring.

#### Verify the labels on all panels, field devices, and process equipment for consistency and completeness of all documents.

#### Verify and document network physical integrity.  Refer to the technical specifications in the Contract Documents for detailed requirements.

### Mechanical Equipment Commissioning shall be performed, including the following, per the manufacturer’s documentation and the technical specifications:

#### Verify that all equipment and components have been fully and properly installed.

#### Verify mechanical connections, fittings and mountings.

#### Verify equipment alignment.

## COMMISSIONING

### Commissioning may begin two (2) weeks after approval of each applicable Commissioning Plan, subject to the following stipulations:

#### In accordance with Commissioning Requirements and Sequence, Section 01 75 00, Commissioning shall only be initiated subsequent to all prior work being approved.

#### The CONTRACTOR shall notify the CITY at least eight (8) work hours prior to each Commissioning activity.  To minimize facility disruptions, all Commissioning activities shall be coordinated in advance with the CITY.  At the CITY’s discretion, the CITY may elect to witness some or all of these activities.

#### Once started, Commissioning shall continue or be repeated until successful completion is accomplished.  All requests to interrupt, suspend or restart Commissioning activities shall be submitted for approval.

### Commissioning of completed systems shall be in accordance with the scheduling requirements of Testing Laboratory Services, Sections 01 45 29 and Commissioning, as described in this Section.  As such, it shall be necessary to perform multiple commissioning periods.

### The CITY’s personnel will be responsible for operation of the equipment and systems to be commissioned.  The portion of the Work to be commissioned shall be fully operational, performing all functions for which it was designed.

### During the commissioning period, the CITY shall be responsible for all normal operational costs and the CONTRACTOR shall bear the costs of all necessary repairs or replacements, including labor and materials, required to keep the portion of the plant being commissioned, operational. CONTRACTOR shall document and complete all required maintenance as specified by the manufacturer. The CITY will take over maintenance when the Project achieves Substantial Completion.

### The date on which the commissioning period is successfully completed shall be noted by the CITY in writing to the CONTRACTOR.

### If any Equipment Commissioning cannot be completed successfully, necessary modifications, adjustments, repairs or field engineering shall be performed as required for successful completion.  Equipment Commissioning shall continue or be repeated until successful completion is accomplished.

### Any proposed deviation from the approved plans or schedules shall require written authorization by the CITY.

## DOCUMENTATION

### Only the forms and documents submitted to and approved by CITY shall be used to document field Equipment Commissioning.  As each activity is completed, all forms shall be completed, dated and signed by the CONTRACTOR.

### The CONTRACTOR shall maintain a list of Commissioning deficiencies, which shall be updated and sent to the CITY at the end of each week during Commissioning.  All deficiencies shall be corrected prior to submittal of any completed documentation for approval.

### Upon completion of all Commissioning, all completed and witnessed documents shall be compiled and formally submitted for approval.

### The CONTRACTOR shall complete and submit a final checklist of the maintenance activities performed, including dates, times, and responsible parties once the Project or individual equipment achieve Substantial Completion.

PART 4 – FLOW CHART

Refer to 01 75 00 Section 2 for the 30-Day Commissioning Reliability Test workflow.

END OF SECTION 01 75 06

THIS PAGE LEFT BLANK INTENTIONALLY